|  |
| --- |
| Declaration of Performance |
| **No. 002a-DOP-2024-03-25** |

|  |  |  |
| --- | --- | --- |
| 1. | Unique identification code of the product-type: | **Multi-wall Metal System Chimney (with 316L Liner)****ICS 50 (inc. painted products)** |
| 2. | Intended use: | **Convey the products of combustion from heating appliances to the outside atmosphere** |
| 3. | Product designations: | Model 1 | DN (80 – 300) | **T600 N1 W V2 L50050 G25** |
|  |  |  | DN (350 - 450) | **T600 N1 W V2 L50050 G37,5** |
|  |  |  | DN (500 - 600) | **T600 N1 W V2 L50050 G50** |
|  |  |  | DN (650 - 1200) | **T600 N1 W V2 L50050 G100** |
|  |  |  |  |  |
|  |  | Model 2 | DN (80 – 300) | **T600 N1 D V3 L50050 G25** |
|  |  |  | DN (350 - 450) | **T600 N1 D V3 L50050 G37,5** |
|  |  |  | DN (500 - 600) | **T600 N1 D V3 L50050 G50** |
|  |  |  | DN (650 - 1200) | **T600 N1 D V3 L50050 G100** |
|  |  |  |  |  |
|  |  | Model 3 | DN (80 – 300) | **T400 N1 W V2 L50050 G25** |
|  |  |  | DN (350 - 450) | **T400 N1 W V2 L50050 G37,5** |
|  |  |  | DN (500 - 600) | **T400 N1 W V2 L50050 G50** |
|  |  |  | DN (650 - 1200) | **T400 N1 W V2 L50050 G100** |
|  |  |  |  |  |
|  |  | Model 4 | DN (80 – 300) | **T400 N1 D V3 L50050 G25** |
|  |  |  | DN (350 - 450) | **T400 N1 D V3 L50050 G37,5** |
|  |  |  | DN (500 - 600) | **T400 N1 D V3 L50050 G50** |
|  |  |  | DN (650 - 1200) | **T400 N1 D V3 L50050 G100** |
|  |  |  |  |  |
|  |  | Model 5 | DN (80 - 700) | **T200 P1 W V2 L50050 O00** |
|  |  |  |
| 4. | Manufacturer: | **Schiedel s.r.o.,** **Horoušanská 286,** **CZ-250 81 Nehvizdy** |
| 5. | Authorized representative: | **N/A** |
| 6. | System(s) of AVCP: | **System 2+** (and System 4 for terminals) |
| 7. | Harmonized standard: | **EN 1856-1:2009** |
|  | Notified body: | **0036** |

8. Declared performance:

|  |  |  |
| --- | --- | --- |
| **Essential characteristics** | **Performance** | **Harmonized technical specification** |
| Compressive strength  | Model(s) 1 to 5: DN (80 – 300): **15 m**DN (350 - 700): **10 m**DN (750 - 1200): **NPD** | EN 1856-1: 2009 |
| Chimney sections, fittings and supports | For further information see installation instructions |
| Resistance to fire | Model(s) 1, 2:DN (80 – 300): **T600 G25**DN (350 - 450): **T600 G37,5**DN (500 - 600): **T600 G50**DN (650 - 1200): **T600 G100**\*Tested fully ventilatedModel(s) 3, 4: DN (80 – 300): **T400 G25**DN (350 - 450): **T400 G37,5**DN (500 - 600): **T400 G50**DN (650 - 1200): **T400 G100**\*Tested fully ventilatedModel 5: DN (80 – 700) : **T200 O00**\*Tested non-enclosed; floor penetration fully insulated with solid fire-stop plates.  | EN 1856-1: 2009 |
| Gas tightness /leakage | Model(s) 1, 2, 3, 4:DN (80 – 1200): **N1**Model 5:DN (80 – 700): **P1** | EN 1856-1: 2009 |
| Flow resistance of chimney sections | Model(s) 1 to 5: DN (80 – 1200): **1,0 mm** | EN 1856-1: 2009 |
| Flow resistance of chimney fittings Flow resistance of terminals | **Zeta 0.3** according EN 13384-1**Zeta 0.5** according EN 13384-1 | EN 13384-1: 2014 |
| Thermal resistance | Model(s) 1 to 5:DN (80 – 1200): **0.56 m2 K/W** tested at 200°C | EN 1856-1: 2009 |
| Thermal shock resistance  |  | EN 1856-1: 2009 |
| Sootfire Resistance: | Model(s) 1, 2, 3, 4:DN (80 – 1200): **Yes**Model 5:DN (80 – 700): **No** |
| Thermal performance under normal operating conditions: | Model(s) 1, 2: DN (80 – 1200): **T600**Model(s) 3, 4: DN (80 – 1200): **T400**Model 5: DN (80 – 700): **T200** |

|  |  |  |
| --- | --- | --- |
| **Essential characteristics** | **Performance** | **Harmonized technical specification** |
| Flexural tensile strength (only for means of connection for chimney sections and fittings) | Model(s) 1 to 5:DN 80 = **33 m** DN 300 = **12** mDN 700 = **3 m** DN 1200 = **NPD** | EN 1856-1: 2009 |
| Non-vertical installation  | Model(s) 1 to 5: DN (80 – 500): between supports **≤ 3 m at 90°**DN (550 - 700): between supports **≤ 4 m at 90°**DN (750 - 1200): **NPD** | EN 1856-1: 2009 |
| Components subject to wind load | Model(s) 1 to 5: DN (80 – 400): **≤ 3 m** above last support **≤ 4 m** between supportsDN (450 - 700): **≤ 2 m** above last support **≤ 3 m** between supportsDN (750 - 1200): **NPD** | EN 1856-1: 2009 |
| Durability |  | EN 1856-1: 2009 |
| Water and vapour diffusion resistance  | Model(s) 1, 3, 5:DN (80 – 1200): **Yes**Model(s) 2 & 4:DN (80 – 1200) : **No** |
| Condensate penetration resistance | Model(s) 1, 3, 5:DN (80 – 1200): **Yes**Model(s) 2, 4:DN (80 – 1200) : **No** |
| Durability against corrosion  | Model(s) 1, 3, 5:DN (80 – 1200): **V2**Model(s) 2 & 4:DN (80 – 1200): **V3** |
| Freeze-thaw resistance | Model(s) 1 to 5:DN (80 – 1200): **Yes** |

The performance of the product identified above is in conformity with the set of declared performance/s. This declaration of performance is issued in accordance with Regulation (EU) No 305/2011, under the sole responsibility of the manufacturer identified above.

Signed for and on behalf of the manufacturer by:

Teplice, 25.03.2024 Ivana Černa,

 Plant manager